## Embedded_PC
Technical data | CX2043
Processor | AMD Ryzen™ V1807B 3.35 GHz
Number of cores | 4
Flash memory | slot for CFast card, card not included
Main memory | 8 GB DDR4 RAM (expandable ex factory to 32 GB)
Interfaces | 2 x RJ45 10/100/1000 Mbit/s, 1 x DVI-D, 4 x USB 3.2 Gen. 2, 1 x optional interface
Cooling | integrated fan with ball bearings and speed monitoring
Diagnostics LED | 1 x power, 1 x TC status, 1 x flash access, 2 x bus status
Clock | internal battery-backed clock for time and date (battery exchangeable)
Operating system | Windows 10 IoT Enterprise 2019 LTSC, Windows 10 IoT Enterprise 2021 LTSC, Windows 11 IoT Enterprise 2024 LTSC, TwinCAT/BSD, Beckhoff RT Linux®
Control software | TwinCAT 2 runtime
TwinCAT 3 runtime (XAR)
I/O connection | via power supply module (E-bus or K-bus, automatic recognition)
Power supply | 24 V DC (-15%/+20%)
UPS OCT-capable | yes (depending on power supply unit)
NOVRAM | 128 kB
Max. power consumption | 70 W
Weight | approx. 1230 g
Dimensions (W x H x D) | 144 mm x 99 mm x 91 mm
Relative humidity | 95%, no condensation
Operating temperature | -25…+60°C
Storage temperature | -40…+85°C
Vibration/shock resistance | conforms to EN 60068-2-6/EN 60068-2-27
EMC immunity/emission | conforms to EN 61000-6-2/EN 61000-6-4
Protection rating | IP20
Approvals/markings | CE, UL

## Measurement_device
Technical data | EL3475
Number of inputs | 12
Wiring | 2-conductor
Oversampling factor | –
Distributed Clocks | optional (required for distributed power measurement)
Refresh Interval | U/I RMS values 10 ms at 50 Hz and 100 ms for all other values such as harmonics
Measured values | Current (with SVL or via DPM: voltage, active power, reactive power, apparent power, active energy, reactive energy, apparent energy, cos φ, frequency, THD, power quality factor, harmonic (up to the 62nd harmonic))
Measuring voltage | via SVL
Measuring current | via SCL
Measurement error/uncertainty | 0.3 % based on the measuring range final value (I), 0.6 % calculated values (see documentation)
Update time | Network-synchronous
Monitoring function | Under/over currents (adjustable)
Separation of potential | 2500 V
E-Bus Power Consumption | Typ. 150 mA
Power Consumption Power Contacts | –
Special features | Distributed power measurement (DPM), electronic nameplates readable
Weight | approx. 75 g
Operating Temperature | 0… 55 °C
Storage Temperature | -25...+85 °C
Relative humidity | 95% without condensation
Vibration/shock resistance | according to EN 60068-2-6/EN 60068-2-27
Approvals/Markings | CE

## Current_transformer
Technical data | SCL6123-0040
Accuracy class | 0,5
Primary current | 40 A AC
Frequency | 50… 400 Hz
Electronic nameplate | Yes
Secondary signal | 333 mV
Max. diameter round conductor | 6 mm
Size | 2
Dimensions (W x H x D) | 33.3 mm x 43.5 mm x 30.4 mm
Weight | approx. 320 g
Operating Temperature | -40...+70 °C
Storage Temperature | -45...+85 °C
Relative humidity | 95% without condensation
Approvals/Markings | CE

## Voltage_transformer
Technical data | SVL1323
Measuring voltage | 277 V ULN, 480 V ULL
Measurement category/surge category | 600 V CAT III, (in preparation: 300 V CAT IV), according to EN61010-2-030
Accuracy class | 0,5
Electronic nameplate | Yes
Secondary signal | 333 mV
Dimensions (W x H x D) | 34 mm x 20.8 mm x 98.4 mm
Weight | approx. 45 g
Operating Temperature | -40...+65 °C
Storage Temperature | -45...+85 °C
Relative humidity | 95% without condensation
Approvals/Markings | CE